## park_center_2019_updated
Hourly Energy Calculation Input Page
Legend:
User Input: Select from dropdown menu
User input: Value or specification
Constants
Note: | 1. If the location of the building is changed, follow the instructions in the "Weather Data Converter" section in the REF tab. The climate data converter file ("BEM_Weather_ Data_Converter.xlsb") must be located in the same folder.
|  |  |  | Internal Heat Gain | Monthly
| Building General |  |  | Zone | Zone1 | Zone2 | Zone3 | Zone4 | Zone5 | Zone6 | Zone7 | Zone8 | Zone9 | Zone10 | Garage
| Building Location | Location_Name |  | Space Name | Office
| Nearest Weather Data Source | 2017_AMY_CRC_Data.epw | Follow 'Note 1' above if location is changed | Gross Floor Area (m2) | 54348 | [9 empty] | 0
| Distance between bldg location and weather station (km) | 0 |  | Occupancy (m2/person) | 28.05
| Building Name | Building_Name |  | Metabolic rate (W/person) | 105
| Terrain class | Urban / City |  | Appliance (W/m2) | 13.16 | [9 empty] | 2
| Building total Ventilated volume [m3] | 232920 |  | Lighting (W/m2) | 11.19 | [9 empty] | 8
| Building Height [m] | 90 |  | Outdoor Air (liter/s/person) | 8.33
|  |  |  | DHW (liter/m2/month) | 1.78
| Heat Capacity |  |  | Note: Garage elec use only needs gross floor area, appliance, lighting power density inputs. It doesn't affect the thermal need calculation. It is assumed that appliance and lighting in the garage are always on.
| Envelope Heat Capacity (J/K) | Heavy: 260,000 * Af |  | Building Temperature Set-point Schedule | [5 empty] | Zone 1 Schedule | [7 empty] | Zone 2 Schedule | [6 empty] | Zone 3 Schedule | [6 empty] | Zone 4 Schedule | [6 empty] | Zone 5 Schedule | [6 empty] | Zone 6 Schedule | [6 empty] | Zone 7 Schedule | [6 empty] | Zone 8 Schedule | [6 empty] | Zone 9 Schedule | [6 empty] | Zone 10 Schedule
|  |  |  | Hour | WD_Tset_heat | WE_Tset_heat | WD_Tset_cool | WE_Tset_cool |  | Hour | Occ_WD | Occ_WE | App_WD | App_WE | Light_WD | Light_WE |  | Hour | Occ_WD | Occ_WE | App_WD | App_WE | Light_WD | Light_WE | Hour | Occ_WD | Occ_WE | App_WD | App_WE | Light_WD | Light_WE | Hour | Occ_WD | Occ_WE | App_WD | App_WE | Light_WD | Light_WE | Hour | Occ_WD | Occ_WE | App_WD | App_WE | Light_WD | Light_WE | Hour | Occ_WD | Occ_WE | App_WD | App_WE | Light_WD | Light_WE | Hour | Occ_WD | Occ_WE | App_WD | App_WE | Light_WD | Light_WE | Hour | Occ_WD | Occ_WE | App_WD | App_WE | Light_WD | Light_WE | Hour | Occ_WD | Occ_WE | App_WD | App_WE | Light_WD | Light_WE | Hour | Occ_WD | Occ_WE | App_WD | App_WE | Light_WD | Light_WE
| Building System |  |  | 0-1 | 15.6 | 15.6 | 29.4 | 29.4 |  | 0-1 | - | - | 0.1 | 0.1 | - | - |  | 0-1 | [6 empty] | 0-1 | [6 empty] | 0-1 | [6 empty] | 0-1 | [6 empty] | 0-1 | [6 empty] | 0-1 | [6 empty] | 0-1 | [6 empty] | 0-1 | [6 empty] | 0-1
| Lighting |  |  | 2021-01-02 | 15.6 | 15.6 | 29.4 | 29.4 |  | 2021-01-02 | - | - | 0.1 | 0.1 | - | - |  | 2021-01-02 | [6 empty] | 2021-01-02 | [6 empty] | 2021-01-02 | [6 empty] | 2021-01-02 | [6 empty] | 2021-01-02 | [6 empty] | 2021-01-02 | [6 empty] | 2021-01-02 | [6 empty] | 2021-01-02 | [6 empty] | 2021-01-02
| Lighting daylighting factor | 1 | No Control: 1, Range (0=< factor =<1) | 2021-02-03 | 15.6 | 15.6 | 29.4 | 29.4 |  | 2021-02-03 | - | - | 0.1 | 0.1 | - | - |  | 2021-02-03 | [6 empty] | 2021-02-03 | [6 empty] | 2021-02-03 | [6 empty] | 2021-02-03 | [6 empty] | 2021-02-03 | [6 empty] | 2021-02-03 | [6 empty] | 2021-02-03 | [6 empty] | 2021-02-03 | [6 empty] | 2021-02-03
| Lighting occupancy factor | 1 | No Control: 1, Range (0=< factor =<1) | 2021-03-04 | 15.6 | 15.6 | 29.4 | 29.4 |  | 2021-03-04 | - | - | 0.1 | 0.1 | - | - |  | 2021-03-04 | [6 empty] | 2021-03-04 | [6 empty] | 2021-03-04 | [6 empty] | 2021-03-04 | [6 empty] | 2021-03-04 | [6 empty] | 2021-03-04 | [6 empty] | 2021-03-04 | [6 empty] | 2021-03-04 | [6 empty] | 2021-03-04
| Lighting constant illumination control factor | 1 | No Control: 1, Range (0=< factor =<1) | 2021-04-05 | 15.6 | 15.6 | 29.4 | 29.4 |  | 2021-04-05 | - | - | 0.1 | 0.1 | - | - |  | 2021-04-05 | [6 empty] | 2021-04-05 | [6 empty] | 2021-04-05 | [6 empty] | 2021-04-05 | [6 empty] | 2021-04-05 | [6 empty] | 2021-04-05 | [6 empty] | 2021-04-05 | [6 empty] | 2021-04-05 | [6 empty] | 2021-04-05
| Is parasitic lighting energy considered? | Yes | Refer to REF sheet | 2021-05-06 | 15.6 | 15.6 | 29.4 | 29.4 |  | 2021-05-06 | - | - | 0.1 | 0.1 | - | - |  | 2021-05-06 | [6 empty] | 2021-05-06 | [6 empty] | 2021-05-06 | [6 empty] | 2021-05-06 | [6 empty] | 2021-05-06 | [6 empty] | 2021-05-06 | [6 empty] | 2021-05-06 | [6 empty] | 2021-05-06 | [6 empty] | 2021-05-06
| Annual parasitic energy for emergency lighting and automatic lighting controls (kWh/m2/yr) | 6 | Refer to REF sheet | 2021-06-07 | 22.2 | 15.6 | 23.9 | 29.4 |  | 2021-06-07 | 1 | 0.1 | 1 | 0.1 | 1 | 0.1 |  | 2021-06-07 | [6 empty] | 2021-06-07 | [6 empty] | 2021-06-07 | [6 empty] | 2021-06-07 | [6 empty] | 2021-06-07 | [6 empty] | 2021-06-07 | [6 empty] | 2021-06-07 | [6 empty] | 2021-06-07 | [6 empty] | 2021-06-07
| Heating and Cooling Plants |  |  | 2021-07-08 | 22.2 | 15.6 | 23.9 | 29.4 |  | 2021-07-08 | 1 | 0.1 | 1 | 0.1 | 1 | 0.1 |  | 2021-07-08 | [6 empty] | 2021-07-08 | [6 empty] | 2021-07-08 | [6 empty] | 2021-07-08 | [6 empty] | 2021-07-08 | [6 empty] | 2021-07-08 | [6 empty] | 2021-07-08 | [6 empty] | 2021-07-08 | [6 empty] | 2021-07-08
| Heating System Coefficient of Performance (COP) [KW/KW] | 0.91 |  | 2021-08-09 | 22.2 | 22.2 | 23.9 | 23.9 |  | 2021-08-09 | 1 | 0.15 | 1 | 0.1 | 1 | 0.15 |  | 2021-08-09 | [6 empty] | 2021-08-09 | [6 empty] | 2021-08-09 | [6 empty] | 2021-08-09 | [6 empty] | 2021-08-09 | [6 empty] | 2021-08-09 | [6 empty] | 2021-08-09 | [6 empty] | 2021-08-09 | [6 empty] | 2021-08-09
| Cooling System Full Load COP [KW/KW] | 4.9 | IPLV: 0.82, Seasonal COP: 4 | 2021-09-10 | 22.2 | 22.2 | 23.9 | 23.9 |  | 2021-09-10 | 1 | 0.15 | 1 | 0.1 | 1 | 0.15 |  | 2021-09-10 | [6 empty] | 2021-09-10 | [6 empty] | 2021-09-10 | [6 empty] | 2021-09-10 | [6 empty] | 2021-09-10 | [6 empty] | 2021-09-10 | [6 empty] | 2021-09-10 | [6 empty] | 2021-09-10 | [6 empty] | 2021-09-10
| Relative COP100: for Relative Load 100% | 1 | Refer to REF sheet | 2021-10-11 | 22.2 | 22.2 | 23.9 | 23.9 |  | 2021-10-11 | 1 | 0.15 | 1 | 0.1 | 1 | 0.15 |  | 2021-10-11 | [6 empty] | 2021-10-11 | [6 empty] | 2021-10-11 | [6 empty] | 2021-10-11 | [6 empty] | 2021-10-11 | [6 empty] | 2021-10-11 | [6 empty] | 2021-10-11 | [6 empty] | 2021-10-11 | [6 empty] | 2021-10-11
| Partial Load COP75 Relative Load 75% | 0.9 | Refer to REF sheet | 2021-11-12 | 22.2 | 22.2 | 23.9 | 23.9 |  | 2021-11-12 | 1 | 0.15 | 1 | 0.1 | 1 | 0.15 |  | 2021-11-12 | [6 empty] | 2021-11-12 | [6 empty] | 2021-11-12 | [6 empty] | 2021-11-12 | [6 empty] | 2021-11-12 | [6 empty] | 2021-11-12 | [6 empty] | 2021-11-12 | [6 empty] | 2021-11-12 | [6 empty] | 2021-11-12
| Partial Load COP50 Relative Load 50% | 0.82 | Refer to REF sheet | 2021-12-13 | 22.2 | 22.2 | 23.9 | 23.9 |  | 2021-12-13 | 1 | 0.15 | 1 | 0.1 | 1 | 0.15 |  | 2021-12-13 | [6 empty] | 2021-12-13 | [6 empty] | 2021-12-13 | [6 empty] | 2021-12-13 | [6 empty] | 2021-12-13 | [6 empty] | 2021-12-13 | [6 empty] | 2021-12-13 | [6 empty] | 2021-12-13 | [6 empty] | 2021-12-13
| Partial Load COP25 Relative Load 25% | 0.5 | Refer to REF sheet | 13-14 | 22.2 | 15.6 | 23.9 | 29.4 |  | 13-14 | 1 | 0.05 | 1 | 0.1 | 1 | 0.05 |  | 13-14 | [6 empty] | 13-14 | [6 empty] | 13-14 | [6 empty] | 13-14 | [6 empty] | 13-14 | [6 empty] | 13-14 | [6 empty] | 13-14 | [6 empty] | 13-14 | [6 empty] | 13-14
| Weighting of 100% Load | 0.01 | From ARI 550/590 Standard | 14-15 | 22.2 | 15.6 | 23.9 | 29.4 |  | 14-15 | 1 | 0.05 | 1 | 0.1 | 1 | 0.05 |  | 14-15 | [6 empty] | 14-15 | [6 empty] | 14-15 | [6 empty] | 14-15 | [6 empty] | 14-15 | [6 empty] | 14-15 | [6 empty] | 14-15 | [6 empty] | 14-15 | [6 empty] | 14-15
| Weighting of 75% Load | 0.42 | From ARI 550/590 Standard | 15-16 | 22.2 | 15.6 | 23.9 | 29.4 |  | 15-16 | 1 | 0.05 | 1 | 0.1 | 1 | 0.05 |  | 15-16 | [6 empty] | 15-16 | [6 empty] | 15-16 | [6 empty] | 15-16 | [6 empty] | 15-16 | [6 empty] | 15-16 | [6 empty] | 15-16 | [6 empty] | 15-16 | [6 empty] | 15-16
| Weighting of 50% Load | 0.45 | From ARI 550/590 Standard | 16-17 | 22.2 | 15.6 | 23.9 | 29.4 |  | 16-17 | 1 | 0.05 | 1 | 0.1 | 1 | 0.05 |  | 16-17 | [6 empty] | 16-17 | [6 empty] | 16-17 | [6 empty] | 16-17 | [6 empty] | 16-17 | [6 empty] | 16-17 | [6 empty] | 16-17 | [6 empty] | 16-17 | [6 empty] | 16-17
| Weighting of 25% Load | 0.12 | From ARI 550/590 Standard | 17-18 | 22.2 | 15.6 | 23.9 | 29.4 |  | 17-18 | 1 | 0.05 | 1 | 0.1 | 1 | 0.05 |  | 17-18 | [6 empty] | 17-18 | [6 empty] | 17-18 | [6 empty] | 17-18 | [6 empty] | 17-18 | [6 empty] | 17-18 | [6 empty] | 17-18 | [6 empty] | 17-18 | [6 empty] | 17-18
| HVAC System |  |  | 18-19 | 15.6 | 15.6 | 29.4 | 29.4 |  | 18-19 | 0.1 | - | 0.1 | 0.1 | 0.1 | - |  | 18-19 | [6 empty] | 18-19 | [6 empty] | 18-19 | [6 empty] | 18-19 | [6 empty] | 18-19 | [6 empty] | 18-19 | [6 empty] | 18-19 | [6 empty] | 18-19 | [6 empty] | 18-19
| HVAC system type: (System / Heat distrition by / Cold distribution by / room temp. cntrl) | 22. Variable air volume / Water or Water&Air / Water / Yes |  | 19-20 | 15.6 | 15.6 | 29.4 | 29.4 |  | 19-20 | 0.1 | - | 0.1 | 0.1 | 0.1 | - |  | 19-20 | [6 empty] | 19-20 | [6 empty] | 19-20 | [6 empty] | 19-20 | [6 empty] | 19-20 | [6 empty] | 19-20 | [6 empty] | 19-20 | [6 empty] | 19-20 | [6 empty] | 19-20
| Ventilation and Cooling type | 1. Mechanical system only; no provision for natural ventilation |  | 20-21 | 15.6 | 15.6 | 29.4 | 29.4 |  | 20-21 | 0.1 | - | 0.1 | 0.1 | 0.1 | - |  | 20-21 | [6 empty] | 20-21 | [6 empty] | 20-21 | [6 empty] | 20-21 | [6 empty] | 20-21 | [6 empty] | 20-21 | [6 empty] | 20-21 | [6 empty] | 20-21 | [6 empty] | 20-21
| Relative Humidity threshold for outside air cooling - upper limit (%) | 75 |  | 21-22 | 15.6 | 15.6 | 29.4 | 29.4 |  | 21-22 | 0.1 | - | 0.1 | 0.1 | 0.1 | - |  | 21-22 | [6 empty] | 21-22 | [6 empty] | 21-22 | [6 empty] | 21-22 | [6 empty] | 21-22 | [6 empty] | 21-22 | [6 empty] | 21-22 | [6 empty] | 21-22 | [6 empty] | 21-22
| Extra ventilation above fresh air supply (liter/s) | 0 | (Only used for extra fan energy consumption) | 22-23 | 15.6 | 15.6 | 29.4 | 29.4 |  | 22-23 | 0.1 | - | 0.1 | 0.1 | 0.1 | - |  | 22-23 | [6 empty] | 22-23 | [6 empty] | 22-23 | [6 empty] | 22-23 | [6 empty] | 22-23 | [6 empty] | 22-23 | [6 empty] | 22-23 | [6 empty] | 22-23 | [6 empty] | 22-23
| Heat recovery type | Slowly rotating or intermittent heat exchangers (0.7) |  | 23-24 | 15.6 | 15.6 | 29.4 | 29.4 |  | 23-24 | 0.1 | - | 0.1 | 0.1 | 0.1 | - |  | 23-24 | [6 empty] | 23-24 | [6 empty] | 23-24 | [6 empty] | 23-24 | [6 empty] | 23-24 | [6 empty] | 23-24 | [6 empty] | 23-24 | [6 empty] | 23-24 | [6 empty] | 23-24
| Exhaust air recirculation percentage | Exhaust air recirculation 20% |  | Note: WD: Weekday, WE: Weekend, Tset,heat: Heating set-point temperature, Tset,cool: Cooling set-point temperature, Occ: Occupant, App: Appliance, Light: Lighting
| Building air leakage level (Air flow m3/h per floor area at Q4Pa) | 1 | Refer to REF sheet (Infiltration ACH: 0.24)
| Specifiec fan power [W/(l/s)] | 2.5 | Average electromotor efficiency: Refer to REF sheet
| Fan flow control factor | 0.65 | Average control reduction factor: Refer to REF sheet | Envelope
| Pump control for cooling | Automatic control more than 50% |  |  | Oqaque1 | Oqaque2 | Window 1 |  |  |  |  | Window 2 |  |  |  |  | Natural Ventilation
| Pump control for heating | All other cases |  | Orientation | Area [m2] | Area [m2] | Area [m2] | Window1 Overhang Angle [degree] | Window1 Fin Angle [degree] | Window1 Horizon Angle [degree] | SRF | Area [m2] | Window1 Overhang Angle [degree] | Window1 Fin Angle [degree] | Window1 Horizon Angle [degree] | SRF2 | NV Window Input
| Domestic Hot Water System |  |  | S | 1818 |  | 3613.8 |  | - | - | 0.55752 | - |  |  |  | 1 | Width [m] |  | -
| DHW Distribution System | Taps More Than 3m from Heat Generation |  | SE | - | [5 empty] | 0.55752 | - |  |  |  | 1 | Height [m] |  | -
| DHW Generation System | Electric (0.75) |  | E | 881.2 |  | 1751.6 |  | - |  | 0.55752 | - |  |  |  | 1 | Effective Angle |  | 270
| Building Energy Management System |  |  | NE | 2031.8 |  | 4038.7 |  |  |  | 0.55752 | - |  |  |  | 1 | Wind direction in degrees (N = 0 or 360, E = 90, S = 180, W = 270).
| Type of BEM system installed | 2 | Refer to REF sheet | N | 1955.6 |  | 3887.3 |  | - |  | 0.55752 | - |  |  |  | 1
|  |  |  | NW | - | [5 empty] | 0.55752 | - |  |  |  | 1
| Bldg Integrated Energy Generation System |  |  | W | 873.9 |  | 1737.1 |  | - |  | 0.55752 | - |  |  |  | 1
| Photovoltaic System |  |  | SW | 2412.9 |  | 4796.3 |  |  |  | 0.55752 | - |  |  |  | 1
| PV module Surface Area (m2) | 0 |  | Roof(Hor) | 3792 |  | - |  |  |  | 1 | - |  |  |  | 1
| PV Module Orientation | S |  | Below grade
| PV Module Angle (tilt in degrees) | 30 |  | Refer to REFERENCE sheet for angle inputs for Overhang, Fin, and Horizon. None: 0. | [6 empty] | Electric Vehicle Charger | [13 empty] | Garage Schedule
| PV panel peak power coefficient (kW/m2) | 0.15 | Refer to REF sheet | Refer to REFERENCE sheet for shading device Shading Reduction Factor (SRF) from Internal or External Shading Device (Blind or Curtain). No shading device: 1. | [6 empty] | No. of EV chargers [ea] |  | 0 | Hour | EV_WD | EV_WE | [8 empty] | Hour | App_WD | App_WE | Light_WD | Light_WE
| PV system performance factor (level of ventilation) | 0.7 | Refer to REF sheet | Material | [6 empty] | EV charger power [kW] |  | 20 | 0-1 | 0.05 | 0.05 | [8 empty] | 0-1 | 1 | 1 | 1 | 1
| Solar Water Heating System |  |  | Type | Uvalue [W/m2/K] | Absorption coefficient | Emissivity | Solar Transmittance | [5 empty] | 2021-01-02 | 0.05 | 0.05 | [8 empty] | 2021-01-02 | 1 | 1 | 1 | 1
| Solar Collector Surface Area (m2) | 0 |  | Roof1 | 0.23 | 0.85 | 0.85 | [6 empty] | 2021-02-03 | 0.05 | 0.05 |  | Internal Heat Gain | [6 empty] | 2021-02-03 | 1 | 1 | 1 | 1
| SHW module orientation | S |  | Roof2 | [9 empty] | 2021-03-04 | 0.05 | 0.05 |  | Month | Occupancy (m2/person) | Appliance (W/m2) | Lighting (W/m2) |  |  |  | 2021-03-04 | 1 | 1 | 1 | 1
| SHW module angle (tilt in degrees) | 30 |  | Opaque1 | 0.39 | 0.7 | 0.85 | [6 empty] | 2021-04-05 | 0.05 | 0.05 |  | Jan | 13 | 12 | 10.76 |  |  |  | 2021-04-05 | 1 | 1 | 1 | 1
| Solar Collector Efficiency | 0.5 | From NEN 2916:1998 | Opaque2 | [9 empty] | 2021-05-06 | 0.05 | 0.05 |  | Feb | 14 | 12 | 10.76 |  |  |  | 2021-05-06 | 1 | 1 | 1 | 1
| Wind Turbine System |  |  | Window1 | 1.64 |  | 0.1 | 0.14 | [5 empty] | 2021-06-07 | 0.1 | 0.1 |  | Mar | 14 | 12 | 10.76 |  |  |  | 2021-06-07 | 1 | 1 | 1 | 1
| Wind Turbine diameter [m] | 0 |  | Window2 | [9 empty] | 2021-07-08 | 0.2 | 0.1 |  | Apr | 14 | 13 | 11 |  |  |  | 2021-07-08 | 1 | 1 | 1 | 1
| Wind Turbine efficiency | 0.4 | [11 empty] | 2021-08-09 | 0.95 | 0.1 |  | May | 14 | 13 | 11 |  |  |  | 2021-08-09 | 1 | 1 | 1 | 1
|  |  |  | First day of the year | Tuesday | [8 empty] | 2021-09-10 | 0.95 | 0.1 |  | Jun | 14 | 13 | 11 |  |  |  | 2021-09-10 | 1 | 1 | 1 | 1
| Energy Sources | [12 empty] | 2021-10-11 | 0.95 | 0.1 |  | Jul | 14 | 13 | 11 |  |  |  | 2021-10-11 | 1 | 1 | 1 | 1
| Primary energy source for Heating | Electricity |  | Electric Battery |  |  | Retail | [6 empty] | 2021-11-12 | 0.95 | 0.1 |  | Aug | 14 | 12 | 10.76 |  |  |  | 2021-11-12 | 1 | 1 | 1 | 1
| Primary energy source for DHW | Electricity |  | Battery Capacity [kWh] | 0 |  | refrig appliance capacity (W/m2) |  |  | - |  |  |  | 2021-12-13 | 0.95 | 0.1 |  | Sep | 14 | 12 | 10.76 |  |  |  | 2021-12-13 | 1 | 1 | 1 | 1
| Primary energy source for Cooling | Electricity |  | Charging efficiency [-] | 0.98 |  | Refrig zone |  |  | Zone1 |  |  |  | 13-14 | 0.5 | 0.1 |  | Oct | 12 | 12 | 10.76 |  |  |  | 13-14 | 1 | 1 | 1 | 1
|  |  |  | Discharging efficiency [-] | 0.98 |  | As constant Electric appliancve (always on) | [6 empty] | 14-15 | 0.95 | 0.1 |  | Nov | 12 | 13 | 11 |  |  |  | 14-15 | 1 | 1 | 1 | 1
| Primary and Emission Factor | Primary Energy Factor | CO2 Emission Coefficient [g/kWh] | Charging Power Limit [kW] | 60 |  | Assumed COP of refigeration appliance | [6 empty] | 15-16 | 0.95 | 0.1 |  | Dec | 12 | 13 | 11 |  |  |  | 15-16 | 1 | 1 | 1 | 1
| Electricity | 3.39 | 744 | Discharging Power Limit [kW] | 60 | [8 empty] | 16-17 | 0.95 | 0.1 | [8 empty] | 16-17 | 1 | 1 | 1 | 1
| Natural Gas | 1.09 | 277 | [10 empty] | 17-18 | 0.95 | 0.1 | [8 empty] | 17-18 | 1 | 1 | 1 | 1
| Fuel | 1.19 | 330 | Lighting Dimmer | [9 empty] | 18-19 | 0.7 | 0.1 | [8 empty] | 18-19 | 1 | 1 | 1 | 1
|  |  | * Atlanta, GA | Dimmer Saving _WD [-] | 0 | [8 empty] | 19-20 | 0.4 | 0.1 | [8 empty] | 19-20 | 1 | 1 | 1 | 1
|  |  |  | Dimmer Saving _WE [-] | 0 | [8 empty] | 20-21 | 0.1 | 0.1 | [8 empty] | 20-21 | 1 | 1 | 1 | 1
|  |  |  | i.e., If lighting dimmer saves an additional 30% of lighting energy use, input 0.3. | [9 empty] | 21-22 | 0.1 | 0.1 | [8 empty] | 21-22 | 1 | 1 | 1 | 1
DO NOT DELETE OR REMOVE |  |  |  | i.e., If the lighting dimmer is not installed, input 0, which means there are no additional lighting energy use savings from the dimmer. | [9 empty] | 22-23 | 0.05 | 0.1 | [8 empty] | 22-23 | 1 | 1 | 1 | 1
List for Dropdown Menu | [13 empty] | 23-24 | 0.05 | 0.1 | [8 empty] | 23-24 | 1 | 1 | 1 | 1
Terrain Class
Open terrain
Country
Urban / City
Envelope Heat Capacity Class
Very Light: 80,000 * Af
Light : 110,000 * Af
Medium: 165,000 * Af
Heavy: 260,000 * Af
Very heavy: 370,000 * Af
Parasitic Lighting Energy
Yes
No
HVAC System type (Heat distribution/ Cold distribution/ Room temperature control)
1. No airco system / Water or Water&Air / NA / Yes
2. No airco system / Water or Water&Air / NA / No
3. No airco system / Air / NA / Yes
4. No airco system / Air / NA / No
5. Single duct system / Water or Water&Air / Water / Yes
6 .Single duct system / Water or Water&Air / Air / Yes
7. Single duct system / Water or Water&Air / Air / No
8. Single duct system / Air / Air / Yes
9. Single duct system / Air / Air / No
10. Dual duct system / Water or Water&Air / Water / Yes
11. Dual duct system / Water or Water&Air / Air / Yes
12. Dual duct system / Water or Water&Air / Air / No
13. Dual duct system / Air / Water / Yes
14. Single duct , Terminal reheat / Water or Water&Air / Water / Yes
15. Single duct , Terminal reheat / Water or Water&Air / Air / Yes
16. Single duct , Terminal reheat / Water or Water&Air / Air / No
17. Constant volume / Water or Water&Air / Water / Yes
18. Constant volume / Water or Water&Air / Air / Yes
19. Constant volume / Water or Water&Air / Air / No
20. Constant volume / Air / Air / Yes
21. Constant volume / Air / Air / No
22. Variable air volume / Water or Water&Air / Water / Yes
23. Variable air volume / Water or Water&Air / Air / Yes
24. Variable air volume / Water or Water&Air / Air / No
25. Fan coil system, 2-pipe
26. Fan coil system, 3-pipe
27. Fan coil system, 4-pipe
28. Induction system, 2-pipe non change over
29. Induction system, 2-pipe change over
30. Induction system, 3-pipe
31. Induction system, 4-pipe
32. 2-pipe radiant cooling panels (chilled ceilings & passive chilled beams)
33. 4-pipe radiant cooling panels (chilled ceilings & passive chilled beams)
34. Embedded cooling system floors, walls or ceilings
35. Room units including single duct units
36. Direct expansion single split system
37. Direct expansion single split system including variable refrigerant flow systems
Ventilation fan
1. Mechanical system only; no provision for natural ventilation
2. Mech. w/ optimal natural outside air cooling (whenever possible)
3. Same as 2, with fully natural fresh air supply (always)
Heat recovery system
No heat recovery
Heat exchange plates or pipes (0.65)
Two-elements-system (0.6)
Loading cold with air-conditioning (0.4)
Heat-pipes (0.6)
Slowly rotating or intermittent heat exchangers (0.7)
Exhaust air recirculation %
No exhaust air recirculation
Exhaust air recirculation 20%
Exhaust air recirculation 40%
Exhaust air recirculation 60%
Pump Control for cooling
No pump for cooling
Automatic control more than 50%
All other cases
Pump Control for heating
No pump for heating
Automatic control more than 50%
All other cases
DHW distribution system efficiency
All Taps Within 3m from Heat Generation
Taps More Than 3m from Heat Generation
Circulation system or Unknown
DHW generation system efficiency
Electric (0.75)
VR-Boiler (0.61)
Gas Boiler, HR-Boiler (0.75)
Co-Generation (0.9)
District Heating (0.9)
Heat Pump (1.4)
Steam (0.61)
PV panel peak power coefficient (efficiency) limits
0
1
PV system performance factor (level of ventilation) limits
0
1
Solar Collector Efficiency limits
0
1
Primary Energy Source
Electricity
Natural Gas
Fuel